{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["1"],"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"1","index":0,"n_rows":61,"n_cols":44,"rows_kept":61,"flags":["formulas_cached_only"]}
["所属设备","测点名称","测点描述","测点类型","读写属性","系数K","偏移B","初始值","数值转换","原始值","转换后的值","测点分组","采集类型码","寄存器地址","数据类型","数据格式","按位取值","起始位","终止位","报警使能","历史存储使能","高高报警使能","高报警使能","低报警使能","低低报警使能","高高报警限值","高报警限值","低报警限值","低低报警限值","高高报消息","高报消息","低报消息","低低报消息","报警死区","开关报警","开关报警消息","报警级别","存储方式","存储间隔(秒)","压缩精度","是否上传","PV上传标识","辅助参数","Reserve2"]
["科士达","Ua","ua","模拟量","只读","0.1","0.0","0.0","0","512","1","1","4","3014","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","9","0","0"]
["科士达","Ub","ub","模拟量","只读","0.1","0.0","0.0","0","512","1","1","4","3015","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","10","0","0"]
["科士达","Uc","uc","模拟量","只读","0.1","0.0","0.0","0","512","1","1","4","3016","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","11","0","0"]
["科士达","Fa","f","模拟量","只读","0.01","0.0","0.0","0","512","1","1","4","3017","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","32","0","0"]
["科士达","Fb","B相频率","模拟量","只读","0.01","0.0","0.0","0","512","1","1","4","3018","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","0","-1","0","0"]
["科士达","Fc","C相频率","模拟量","只读","0.01","0.0","0.0","0","512","1","1","4","3019","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","0","-1","0","0"]
["科士达","Ia","ia","模拟量","只读","0.01","0.0","0.0","0","512","1","1","4","3020","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","0","0","0"]
["科士达","Ib","ib","模拟量","只读","0.01","0.0","0.0","0","512","1","1","4","3021","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","1","0","0"]
["科士达","Ic","ic","模拟量","只读","0.01","0.0","0.0","0","512","1","1","4","3022","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","2","0","0"]
["科士达","P","ep","模拟量","只读","0.001","0.0","0.0","0","512","1","1","4","3023","32位有符号","1234","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","17","0","0"]
["科士达","T1","temperature","模拟量","只读","0.1","0.0","0.0","0","512","1","1","4","3025","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","36","0","0"]
["科士达","T2","模块温度","模拟量","只读","0.1","0.0","0.0","0","512","1","1","4","3026","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","-1","0","-1"]
["科士达","ZF","positiveActice","模拟量","只读","0.1","0.0","0.0","0","6","1","1","4","3038","32位无符号","1234","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","240","0","0"]
["科士达","RF","daypositiveActice","模拟量","只读","1.0","0.0","0.0","0","6","1","1","4","3042","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","238","0","0"]
["科士达","S","s","模拟量","只读","0.001","0.0","0.0","0","6","1","2","4","3052","32位有符号","1234","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","0","16","0","0"]
["科士达","Q","eq","模拟量","只读","0.001","0.0","0.0","0","6","1","2","4","3054","32位有符号","1234","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","0","18","0","0"]
["科士达","PF","cos","模拟量","只读","0.001","0.0","0.0","0","6","1","2","4","3056","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","0","28","0","0"]
["科士达","Upv1","uPV1","模拟量","只读","0.1","0.0","0.0","0","512","1","1","4","3000","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","1350","0","1"]
["科士达","Upv2","uPV2","模拟量","只读","0.1","0.0","0.0","0","512","1","1","4","3001","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","2351","0","2"]
["科士达","Upv3","uPV3","模拟量","只读","0.1","0.0","0.0","0","512","1","1","4","3002","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","3352","0","3"]
["科士达","Upv4","uPV4","模拟量","只读","0.1","0.0","0.0","0","512","1","1","4","2996","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","4353","0","4"]
["科士达","Upv5","uPV5","模拟量","只读","0.1","0.0","0.0","0","512","1","1","4","2992","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","5354","0","5"]
["科士达","Upv6","uPV6","模拟量","只读","0.1","0.0","0.0","0","512","1","1","4","2988","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","6355","0","6"]
["科士达","Upv7","uPV7","模拟量","只读","0.1","0.0","0.0","0","512","1","1","4","2984","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","7513","0","7"]
["科士达","Upv8","uPV8","模拟量","只读","0.1","0.0","0.0","0","512","1","1","4","2980","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","8514","0","8"]
["科士达","Upv9","uPV9","模拟量","只读","0.1","0.0","0.0","0","512","1","1","4","2976","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","9627","0","9"]
["科士达","Upv10","uPV10","模拟量","只读","0.1","0.0","0.0","0","512","1","1","4","2972","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","10628","0","10"]
["科士达","Ipv1","iPV1","模拟量","只读","0.01","0.0","0.0","0","512","1","1","4","3003","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","1344","0","1"]
["科士达","Ipv2","iPV2","模拟量","只读","0.01","0.0","0.0","0","512","1","1","4","3004","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","2345","0","2"]
["科士达","Ipv3","iPV3","模拟量","只读","0.01","0.0","0.0","0","512","1","1","4","3005","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","3346","0","3"]
["科士达","Ipv4","iPV4","模拟量","只读","0.01","0.0","0.0","0","512","1","1","4","2997","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","4347","0","4"]
["科士达","Ipv5","iPV5","模拟量","只读","0.01","0.0","0.0","0","512","1","1","4","2993","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","5348","0","5"]
["科士达","Ipv6","iPV6","模拟量","只读","0.01","0.0","0.0","0","512","1","1","4","3028","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","6349","0","6"]
["科士达","Ipv7","iPV7","模拟量","只读","0.01","0.0","0.0","0","512","1","1","4","2985","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","7507","0","7"]
["科士达","Ipv8","iPV8","模拟量","只读","0.01","0.0","0.0","0","512","1","1","4","2981","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","8508","0","8"]
["科士达","Ipv9","iPV9","模拟量","只读","0.01","0.0","0.0","0","512","1","1","4","2977","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","9615","0","9"]
["科士达","Ipv10","iPV10","模拟量","只读","0.01","0.0","0.0","0","512","1","1","4","2973","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","10616","0","10"]
["科士达","F1","市电电压低","开关量","只读","1.0","0.0","0.0","0","512","1","1","4","3028","32位无符号","1234","1","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","100007","0","0"]
["科士达","F2","市电电压高","开关量","只读","1.0","0.0","0.0","0","512","1","1","4","3028","32位无符号","1234","1","1","1","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","100008","0","0"]
["科士达","F3","市电频率低","开关量","只读","1.0","0.0","0.0","0","512","1","1","4","3028","32位无符号","1234","1","2","2","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","100012","0","0"]
["科士达","F4","市电频率高","开关量","只读","1.0","0.0","0.0","0","512","1","1","4","3028","32位无符号","1234","1","3","3","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","100011","0","0"]
["科士达","F5","母线电压低","开关量","只读","1.0","0.0","0.0","0","512","1","1","4","3028","32位无符号","1234","1","4","4","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","100215","0","0"]
["科士达","F6","母线电压高","开关量","只读","1.0","0.0","0.0","0","512","1","1","4","3028","32位无符号","1234","1","5","5","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","100214","0","0"]
["科士达","F7","母线电压不平衡","开关量","只读","1.0","0.0","0.0","0","512","1","1","4","3028","32位无符号","1234","1","6","6","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","100010","0","0"]
["科士达","F8","绝缘阻抗低","开关量","只读","1.0","0.0","0.0","0","512","1","1","4","3028","32位无符号","1234","1","7","7","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","100018","0","0"]
["科士达","F9","输入直流电流高","开关量","只读","1.0","0.0","0.0","0","512","1","1","4","3028","32位无符号","1234","1","8","8","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","0","-1","0","-1"]
["科士达","F10","硬件逆变电流高","开关量","只读","1.0","0.0","0.0","0","512","1","1","4","3028","32位无符号","1234","1","9","9","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","0","-1","0","1"]
["科士达","F11","逆变电流高","开关量","只读","1.0","0.0","0.0","0","512","1","1","4","3028","32位无符号","1234","1","10","10","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","100014","0","0"]
["科士达","F12","逆变电流直流量高","开关量","只读","1.0","0.0","0.0","0","512","1","1","4","3028","32位无符号","1234","1","11","11","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","100269","0","0"]
["科士达","F13","环境温度高","开关量","只读","1.0","0.0","0.0","0","512","1","1","4","3028","32位无符号","1234","1","12","12","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","100019","0","0"]
["科士达","F14","散热器温度高","开关量","只读","1.0","0.0","0.0","0","512","1","1","4","3028","32位无符号","1234","1","13","13","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","0","-1","0","1"]
["科士达","F15","交流继电器异常","开关量","只读","1.0","0.0","0.0","0","512","1","1","4","3028","32位无符号","1234","1","14","14","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","0","-1","0","1"]
["科士达","F16","PV输入电压低","开关量","只读","1.0","0.0","0.0","0","512","1","1","4","3028","32位无符号","1234","1","15","15","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","0","-1","0","-1"]
["科士达","F17","SPI通讯故障","开关量","只读","1.0","0.0","0.0","0","512","1","1","4","3028","32位无符号","1234","1","18","18","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","100045","0","0"]
["科士达","F18","漏电流高","开关量","只读","1.0","0.0","0.0","0","512","1","1","4","3028","32位无符号","1234","1","20","20","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","100259","0","0"]
["科士达","F20","IGBT故障","开关量","只读","1.0","0.0","0.0","0","512","1","1","4","3028","32位无符号","1234","1","26","26","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","100268","0","0"]
["科士达","F22","等待","开关量","只读","1.0","0.0","0.0","1","1","1","3","4","3030","16位无符号","21","1","8","15","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","0","-1","0","1"]
["科士达","F23","正常","开关量","只读","1.0","0.0","0.0","1","3","1","3","4","3030","16位无符号","12","1","8","15","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","0","-1","0","1"]
["科士达","F24","错误","开关量","只读","1.0","0.0","0.0","1","4","1","3","4","3030","16位无符号","21","1","8","15","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","1","100265","0","0"]
["科士达","F25","永久错误","开关量","只读","1.0","0.0","0.0","1","5","1","3","4","3030","16位无符号","21","1","8","15","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","开关变位","通知","0","300","1.0","0","-1","0","1"]