{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["模拟量","开关量"],"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"模拟量","index":0,"n_rows":31,"n_cols":67,"rows_kept":31,"flags":["formulas_cached_only"]}
["设备名称(DevName)","测点名称(TagName)","物模型标识(测点描述)","功能码","读写属性","系数K","偏移B","变量单位","测点分组","寄存器地址","数据类型","高低位顺序","初始值","是否取反","数值转换","原始值","转换值","测点来源","按位取值","取值起始位","取值终止位","报警使能","是否开启高高报警","是否开启高报警","是否开启低报警","是否开启低低报警","高高报警限值","高报警限值","低报警限值","低低报警限值","高高报警消息","高报警消息","低报警消息","低低报警消息","报警死区","开关报警类型","开关报警消息","报警等级","存储使能","存储类型","存储间隔(s)","压缩存储精度","是否上传","辅助参数","PV上传标识","PV上传系数","限值使能位","最大值","最小值","公式计算","控制模式","遥调功能码","遥调寄存器地址","遥调数据类型","遥调字节序","定值组功能码","控分功能码","控分寄存器","控分选择值","控分执行值","控分撤销值","控合功能码","控合寄存器","控合选择值","控合执行值","控合撤销值","Pv码(优先)"]
["科士达设备1","Upv1","PV1 输入电压","0x04号命令(读输入寄存器)","只读","0.1","0.0","--","0","3000","16位无符号","12","0.0","否","否","512","0","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","60","0.5","是","0","直流电压1","10","关","","","","禁用","","","","","","","","","","","","","","","","207"]
["科士达设备2","Upv2","PV2 输入电压","0x04号命令(读输入寄存器)","只读","0.1","0.0","--","0","3001","16位无符号","12","0.0","否","否","512","0","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","60","0.5","是","0","直流电压2","10","关","","","","禁用","","","","","","","","","","","","","","","","225"]
["科士达设备3","Upv3","PV3 输入电压","0x04号命令(读输入寄存器)","只读","0.1","0.0","--","0","3002","16位无符号","12","0.0","否","否","512","0","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","60","0.5","是","0","直流电压3","10","关","","","","禁用","","","","","","","","","","","","","","","","226"]
["科士达设备4","Ipv1","PV1 输入电流","0x04号命令(读输入寄存器)","只读","0.01","0.0","--","0","3003","16位有符号","12","0.0","否","否","512","0","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","60","0.5","是","0","直流电流1","10","关","","","","禁用","","","","","","","","","","","","","","","","208"]
["科士达设备5","Ipv2","PV2 输入电流","0x04号命令(读输入寄存器)","只读","0.01","0.0","--","0","3004","16位有符号","12","0.0","否","否","512","0","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","60","0.5","是","0","直流电流2","10","关","","","","禁用","","","","","","","","","","","","","","","","230"]
["科士达设备6","Ipv3","PV3 输入电流","0x04号命令(读输入寄存器)","只读","0.01","0.0","--","0","3005","16位有符号","12","0.0","否","否","512","0","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","60","0.5","是","0","直流电流3","10","关","","","","禁用","","","","","","","","","","","","","","","","231"]
["科士达设备7","Pv1","PV1 输入功率","0x04号命令(读输入寄存器)","只读","1.0","0.0","--","0","3006","32位有符号","1234","0.0","否","否","512","0","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","60","0.5","是","0","无","1","关","","","","禁用","","","","","","","","","","","","","","","","-1"]
["科士达设备8","Pv2","PV2 输入功率","0x04号命令(读输入寄存器)","只读","1.0","0.0","--","0","3008","32位有符号","1234","0.0","否","否","512","0","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","60","0.5","是","0","无","1","关","","","","禁用","","","","","","","","","","","","","","","","-1"]
["科士达设备9","Pv3","PV3 输入功率","0x04号命令(读输入寄存器)","只读","1.0","0.0","--","0","3010","32位有符号","1234","0.0","否","否","512","0","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","60","0.5","是","0","无","1","关","","","","禁用","","","","","","","","","","","","","","","","-1"]
["科士达设备10","Upb","PBUS 电压","0x04号命令(读输入寄存器)","只读","0.1","0.0","--","0","3012","16位无符号","12","0.0","否","否","512","0","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","60","0.5","是","0","无","1","关","","","","禁用","","","","","","","","","","","","","","","","-1"]
["科士达设备11","Unb","NBUS 电压","0x04号命令(读输入寄存器)","只读","0.1","0.0","--","0","3013","16位无符号","12","0.0","否","否","512","0","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","60","0.5","是","0","无","1","关","","","","禁用","","","","","","","","","","","","","","","","-1"]
["科士达设备12","Urs","RS 相电网电压","0x04号命令(读输入寄存器)","只读","0.1","0.0","--","0","3014","16位无符号","12","0.0","否","否","512","0","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","60","0.5","是","0","A相电压","10","关","","","","禁用","","","","","","","","","","","","","","","","210"]
["科士达设备13","Ust","ST 相电网电压","0x04号命令(读输入寄存器)","只读","0.1","0.0","--","0","3015","16位无符号","12","0.0","否","否","512","0","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","60","0.5","是","0","B相电压","10","关","","","","禁用","","","","","","","","","","","","","","","","211"]
["科士达设备14","Utr","TR 相电网电压","0x04号命令(读输入寄存器)","只读","0.1","0.0","--","0","3016","16位无符号","12","0.0","否","否","512","0","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","60","0.5","是","0","C相电压","10","关","","","","禁用","","","","","","","","","","","","","","","","212"]
["科士达设备15","Frs","RS 电网频率","0x04号命令(读输入寄存器)","只读","0.01","0.0","--","0","3017","16位无符号","12","0.0","否","否","512","0","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","60","0.5","是","0","电网频率","10","关","","","","禁用","","","","","","","","","","","","","","","","222"]
["科士达设备16","Fst","ST 电网频率","0x04号命令(读输入寄存器)","只读","0.01","0.0","--","0","3018","16位无符号","12","0.0","否","否","512","0","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","60","0.5","是","0","无","1","关","","","","禁用","","","","","","","","","","","","","","","","-1"]
["科士达设备17","Ftr","TR 电网频率","0x04号命令(读输入寄存器)","只读","0.01","0.0","--","0","3019","16位无符号","12","0.0","否","否","512","0","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","60","0.5","是","0","无","1","关","","","","禁用","","","","","","","","","","","","","","","","-1"]
["科士达设备18","Ir","R 相并网电流","0x04号命令(读输入寄存器)","只读","0.01","0.0","--","0","3020","16位有符号","12","0.0","否","否","512","0","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","60","0.5","是","0","A相电流","10","关","","","","禁用","","","","","","","","","","","","","","","","213"]
["科士达设备19","Is","S 相并网电流","0x04号命令(读输入寄存器)","只读","0.01","0.0","--","0","3021","16位有符号","12","0.0","否","否","512","0","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","60","0.5","是","0","B相电流","10","关","","","","禁用","","","","","","","","","","","","","","","","214"]
["科士达设备20","It","T 相并网电流","0x04号命令(读输入寄存器)","只读","0.01","0.0","--","0","3022","16位有符号","12","0.0","否","否","512","0","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","60","0.5","是","0","C相电流","10","关","","","","禁用","","","","","","","","","","","","","","","","215"]
["科士达设备21","Pdc","并网功率","0x04号命令(读输入寄存器)","只读","1.0","0.0","--","0","3023","32位有符号","1234","0.0","否","否","512","0","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","模拟量报警","开关变位","通知","否","周期存储","60","0.5","是","0",null,"1","关","","","","禁用","","","","","","","","","","","","","","","","157"]
["科士达设备22","Temp1","散热器温度","0x04号命令(读输入寄存器)","只读","0.1","0.0","--","0","3025","16位无符号","12","0.0","否","否","512","0","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","60","0.5","是","0","无","1","关","","","","禁用","","","","","","","","","","","","","","","","-1"]
["科士达设备23","Temp2","模块温度","0x04号命令(读输入寄存器)","只读","0.1","0.0","--","0","3026","16位无符号","12","0.0","否","否","512","0","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","60","0.5","是","0","机内空气温度","10","关","","","","禁用","","","","","","","","","","","","","","","","204"]
["科士达设备24","TE","总发电量","0x04号命令(读输入寄存器)","只读","0.1","0.0","--","0","3038","32位无符号","1234","0.0","否","否","512","0","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","60","0.5","是","0","总发电量","10","关","","","","禁用","","","","","","","","","","","","","","","","202"]
["科士达设备25","YE","当年发电量","0x04号命令(读输入寄存器)","只读","1.0","0.0","--","0","3040","32位无符号","1234","0.0","否","否","512","0","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","60","0.5","是","0","无","1","关","","","","禁用","","","","","","","","","","","","","","","","-1"]
["科士达设备26","DE","当天发电量","0x04号命令(读输入寄存器)","只读","1.0","0.0","--","0","3042","16位无符号","12","0.0","否","否","512","0","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","60","0.5","是","0","日发电量","10","关","","","","禁用","","","","","","","","","","","","","","","","201"]
["科士达设备27","P","视在功率","0x04号命令(读输入寄存器)","只读","1.0","0.0","--","0","3052","32位有符号","1234","0.0","否","否","512","0","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","60","0.5","是","0","总有功功率","1","关","","","","禁用","","","","","","","","","","","","","","","","219"]
["科士达设备28","Q","无功功率","0x04号命令(读输入寄存器)","只读","1.0","0.0","--","0","3054","32位有符号","1234","0.0","否","否","512","0","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","60","0.5","是","0","总无功功率","1","关","","","","禁用","","","","","","","","","","","","","","","","220"]
["科士达设备29","COS","功率因数","0x04号命令(读输入寄存器)","只读","1.0","0.0","--","0","3056","16位无符号","12","0.0","否","否","512","0","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","60","0.5","是","0","总功率因数","1","关","","","","禁用","","","","","","","","","","","","","","","","221"]
["科士达设备30","Status","状态(--)","0x04号命令(读输入寄存器)","读写","1.0","0.0","--","0","3030","16位有符号","12","0.0","否","否","512","1","采集点","是","8","15","否","否","否","否","否","100.0","90.0","20.0","10.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","300","1.0","是","0","状态","1","关","","","","禁用","","","","","","","","","","","","","","","","224"]

{"sheet":"开关量","index":1,"n_rows":1,"n_cols":67,"rows_kept":1,"flags":["formulas_cached_only"]}
["设备名称(DevName)","测点名称(TagName)","物模型标识(测点描述)","功能码","读写属性","系数K","偏移B","变量单位","测点分组","寄存器地址","数据类型","高低位顺序","初始值","是否取反","数值转换","原始值","转换值","测点来源","按位取值","取值起始位","取值终止位","报警使能","是否开启高高报警","是否开启高报警","是否开启低报警","是否开启低低报警","高高报警限值","高报警限值","低报警限值","低低报警限值","高高报警消息","高报警消息","低报警消息","低低报警消息","报警死区","开关报警类型","开关报警消息","报警等级","存储使能","存储类型","存储间隔(s)","压缩存储精度","是否上传","辅助参数","PV上传标识","PV上传系数","限值使能位","最大值","最小值","公式计算","控制模式","遥调功能码","遥调寄存器地址","遥调数据类型","遥调字节序","定值组功能码","控分功能码","控分寄存器","控分选择值","控分执行值","控分撤销值","控合功能码","控合寄存器","控合选择值","控合执行值","控合撤销值","Pv码(优先)"]