{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["模拟量","开关量"],"not_rendered":{"external_links":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"模拟量","index":0,"n_rows":32,"n_cols":67,"rows_kept":32,"flags":["formulas_cached_only"]}
["设备名称(DevName)","测点名称(TagName)","物模型标识(测点描述)","功能码","读写属性","系数K","偏移B","变量单位","测点分组","寄存器地址","数据类型","高低位顺序","初始值","是否取反","数值转换","原始值","转换值","测点来源","按位取值","取值起始位","取值终止位","报警使能","是否开启高高报警","是否开启高报警","是否开启低报警","是否开启低低报警","高高报警限值","高报警限值","低报警限值","低低报警限值","高高报警消息","高报警消息","低报警消息","低低报警消息","报警死区","开关报警类型","开关报警消息","报警等级","存储使能","存储类型","存储间隔(s)","压缩存储精度","是否上传","辅助参数","PV上传标识","PV上传系数","限值使能位","最大值","最小值","公式计算","控制模式","遥调功能码","遥调寄存器地址","遥调数据类型","遥调字节序","定值组功能码","控分功能码","控分寄存器","控分选择值","控分执行值","控分撤销值","控合功能码","控合寄存器","控合选择值","控合执行值","控合撤销值","Pv码(优先)"]
["INV1","Status","0待机2并网3故障","0x03,0x06号命令(读写保持寄存器)","只读","1.0","0.0","--","0","49168","16位无符号","12","0.0","否","否","4","1","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","300","1.0","是","0","状态","1","关","","","","禁用","","","","","","","","","","","","","","","","224"]
["INV1","Ppv1","支路1功率W","0x03,0x06号命令(读写保持寄存器)","只读","1.0","0.0","--","0","49410","16位无符号","12","0.0","否","否","4","1","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","300","1.0","否","0","无","1","关","","","","禁用","","","","","","","","","","","","","","","","-1"]
["INV1","Ppv2","支路2功率W","0x03,0x06号命令(读写保持寄存器)","只读","1.0","0.0","--","0","49411","16位无符号","12","0.0","否","否","4","1","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","300","1.0","否","0","无","1","关","","","","禁用","","","","","","","","","","","","","","","","-1"]
["INV1","Upv1","支路1电压","0x03,0x06号命令(读写保持寄存器)","只读","0.1","0.0","--","0","49412","16位无符号","12","0.0","否","否","4","1","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","300","1.0","是","0","直流电压1","10","关","","","","禁用","","","","","","","","","","","","","","","","207"]
["INV1","Ipv1","支路1电流","0x03,0x06号命令(读写保持寄存器)","只读","0.1","0.0","--","0","49413","16位无符号","12","0.0","否","否","4","1","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","300","1.0","是","0","直流电流1","10","关","","","","禁用","","","","","","","","","","","","","","","","208"]
["INV1","Upv2","支路2电压","0x03,0x06号命令(读写保持寄存器)","只读","0.1","0.0","--","0","49414","16位无符号","12","0.0","否","否","4","1","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","300","1.0","是","0","直流电压2","10","关","","","","禁用","","","","","","","","","","","","","","","","225"]
["INV1","Ipv2","支路2电流","0x03,0x06号命令(读写保持寄存器)","只读","0.1","0.0","--","0","49415","16位无符号","12","0.0","否","否","4","1","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","300","1.0","是","0","直流电流2","10","关","","","","禁用","","","","","","","","","","","","","","","","230"]
["INV1","Temp1","模块1温度","0x03,0x06号命令(读写保持寄存器)","只读","0.1","0.0","--","0","49417","16位无符号","12","0.0","否","否","4","1","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","300","1.0","是","0","机内散热器温度","10","关","","","","禁用","","","","","","","","","","","","","","","","206"]
["INV1","Temp2","模块2温度","0x03,0x06号命令(读写保持寄存器)","只读","0.1","0.0","--","0","49418","16位无符号","12","0.0","否","否","4","1","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","300","1.0","否","0","无","1","关","","","","禁用","","","","","","","","","","","","","","","","-1"]
["INV1","Ua","电网电压A","0x03,0x06号命令(读写保持寄存器)","只读","0.1","0.0","--","0","49420","16位无符号","12","0.0","否","否","4","1","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","300","1.0","是","0","A相电压","10","关","","","","禁用","","","","","","","","","","","","","","","","210"]
["INV1","Ia","电网电流A","0x03,0x06号命令(读写保持寄存器)","只读","0.1","0.0","--","0","49421","16位无符号","12","0.0","否","否","4","1","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","300","1.0","是","0","A相电流","10","关","","","","禁用","","","","","","","","","","","","","","","","213"]
["INV1","Ub","电网电压B","0x03,0x06号命令(读写保持寄存器)","只读","0.1","0.0","--","0","49422","16位无符号","12","0.0","否","否","4","1","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","300","1.0","是","0","B相电压","10","关","","","","禁用","","","","","","","","","","","","","","","","211"]
["INV1","Ib","电网电流B","0x03,0x06号命令(读写保持寄存器)","只读","0.1","0.0","--","0","49423","16位无符号","12","0.0","否","否","4","1","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","300","1.0","是","0","B相电流","10","关","","","","禁用","","","","","","","","","","","","","","","","214"]
["INV1","Uc","电网电压C","0x03,0x06号命令(读写保持寄存器)","只读","0.1","0.0","--","0","49424","16位无符号","12","0.0","否","否","4","1","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","300","1.0","是","0","C相电压","10","关","","","","禁用","","","","","","","","","","","","","","","","212"]
["INV1","Ic","电网电流C","0x03,0x06号命令(读写保持寄存器)","只读","0.1","0.0","--","0","49425","16位无符号","12","0.0","否","否","4","1","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","300","1.0","是","0","C相电流","10","关","","","","禁用","","","","","","","","","","","","","","","","215"]
["INV1","FreqA","A相频率","0x03,0x06号命令(读写保持寄存器)","只读","0.01","0.0","--","0","49426","16位无符号","12","0.0","否","否","4","1","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","300","1.0","是","0","电网频率","10","关","","","","禁用","","","","","","","","","","","","","","","","222"]
["INV1","FreqB","B相频率","0x03,0x06号命令(读写保持寄存器)","只读","0.01","0.0","--","0","49427","16位无符号","12","0.0","否","否","4","1","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","300","1.0","否","0","无","1","关","","","","禁用","","","","","","","","","","","","","","","","-1"]
["INV1","FreqC","C相频率","0x03,0x06号命令(读写保持寄存器)","只读","0.01","0.0","--","0","49428","16位无符号","12","0.0","否","否","4","1","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","300","1.0","否","0","无","1","关","","","","禁用","","","","","","","","","","","","","","","","-1"]
["INV1","PsumA","A相有功功率W","0x03,0x06号命令(读写保持寄存器)","只读","1.0","0.0","--","0","49429","16位无符号","12","0.0","否","否","4","1","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","300","1.0","是","0","A相有功功率","1","关","","","","禁用","","","","","","","","","","","","","","","","216"]
["INV1","PsumB","B相有功功率W","0x03,0x06号命令(读写保持寄存器)","只读","1.0","0.0","--","0","49430","16位无符号","12","0.0","否","否","4","1","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","300","1.0","是","0","B相有功功率","1","关","","","","禁用","","","","","","","","","","","","","","","","217"]
["INV1","PsumC","C相有功功率W","0x03,0x06号命令(读写保持寄存器)","只读","1.0","0.0","--","0","49431","16位无符号","12","0.0","否","否","4","1","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","300","1.0","是","0","C相有功功率","1","关","","","","禁用","","","","","","","","","","","","","","","","218"]
["INV1","SsumA","A相视在功率VA","0x03,0x06号命令(读写保持寄存器)","只读","1.0","0.0","--","0","49432","16位无符号","12","0.0","否","否","4","1","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","300","1.0","否","0","无","1","关","","","","禁用","","","","","","","","","","","","","","","","-1"]
["INV1","SsumB","B相视在功率VA","0x03,0x06号命令(读写保持寄存器)","只读","1.0","0.0","--","0","49433","16位无符号","12","0.0","否","否","4","1","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","300","1.0","否","0","无","1","关","","","","禁用","","","","","","","","","","","","","","","","-1"]
["INV1","SsumC","C相视在功率VA","0x03,0x06号命令(读写保持寄存器)","只读","1.0","0.0","--","0","49434","16位无符号","12","0.0","否","否","4","1","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","300","1.0","否","0","无","1","关","","","","禁用","","","","","","","","","","","","","","","","-1"]
["INV1","Uab","交流电压UAB","0x03,0x06号命令(读写保持寄存器)","只读","0.1","0.0","--","0","49435","16位无符号","12","0.0","否","否","4","1","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","300","1.0","是","0","线电压Uab","10","关","","","","禁用","","","","","","","","","","","","","","","","235"]
["INV1","Ubc","交流电压UBC","0x03,0x06号命令(读写保持寄存器)","只读","0.1","0.0","--","0","49436","16位无符号","12","0.0","否","否","4","1","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","300","1.0","是","0","线电压Ubc","10","关","","","","禁用","","","","","","","","","","","","","","","","236"]
["INV1","Uca","交流电压UCA","0x03,0x06号命令(读写保持寄存器)","只读","0.1","0.0","--","0","49437","16位无符号","12","0.0","否","否","4","1","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","300","1.0","是","0","线电压Uca","10","关","","","","禁用","","","","","","","","","","","","","","","","237"]
["INV1","Psum","交流侧有功功率W","0x03,0x06号命令(读写保持寄存器)","只读","1.0","0.0","--","0","49438","16位无符号","12","0.0","否","否","4","1","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","300","1.0","是","0","总有功功率","1","关","","","","禁用","","","","","","","","","","","","","","","","219"]
["INV1","Qsum","交流侧无功功率Var","0x03,0x06号命令(读写保持寄存器)","只读","1.0","0.0","--","0","49439","16位无符号","12","0.0","否","否","4","1","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","300","1.0","是","0","总无功功率","1","关","","","","禁用","","","","","","","","","","","","","","","","220"]
["INV1","RF","日发电量kWh","0x03,0x06号命令(读写保持寄存器)","只读","0.001","0.0","--","0","49664","32位无符号","1234","0.0","否","否","4","1","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","300","1.0","是","0","日发电量","10","关","","","","禁用","","","","","","","","","","","","","","","","201"]
["INV1","ZF","总发电量kWh","0x03,0x06号命令(读写保持寄存器)","只读","0.001","0.0","--","0","49666","32位无符号","1234","0.0","否","否","4","1","采集点","否","0","0","否","否","否","否","否","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","变位报警","不报警","通知","否","周期存储","300","1.0","是","0","总发电量","10","关","","","","禁用","","","","","","","","","","","","","","","","202"]

{"sheet":"开关量","index":1,"n_rows":1,"n_cols":67,"rows_kept":1,"flags":["formulas_cached_only"]}
["设备名称(DevName)","测点名称(TagName)","物模型标识(测点描述)","功能码","读写属性","系数K","偏移B","变量单位","测点分组","寄存器地址","数据类型","高低位顺序","初始值","是否取反","数值转换","原始值","转换值","测点来源","按位取值","取值起始位","取值终止位","报警使能","是否开启高高报警","是否开启高报警","是否开启低报警","是否开启低低报警","高高报警限值","高报警限值","低报警限值","低低报警限值","高高报警消息","高报警消息","低报警消息","低低报警消息","报警死区","开关报警类型","开关报警消息","报警等级","存储使能","存储类型","存储间隔(s)","压缩存储精度","是否上传","辅助参数","PV上传标识","PV上传系数","限值使能位","最大值","最小值","公式计算","控制模式","遥调功能码","遥调寄存器地址","遥调数据类型","遥调字节序","定值组功能码","控分功能码","控分寄存器","控分选择值","控分执行值","控分撤销值","控合功能码","控合寄存器","控合选择值","控合执行值","控合撤销值","Pv码(优先)"]