{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["1"],"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"1","index":0,"n_rows":54,"n_cols":44,"rows_kept":54,"flags":["formulas_cached_only"]}
["所属设备","测点名称","测点描述","测点类型","读写属性","系数K","偏移B","初始值","数值转换","原始值","转换后的值","测点分组","采集类型码","寄存器地址","数据类型","数据格式","按位取值","起始位","终止位","报警使能","历史存储使能","高高报警使能","高报警使能","低报警使能","低低报警使能","高高报警限值","高报警限值","低报警限值","低低报警限值","高高报消息","高报消息","低报消息","低低报消息","报警死区","开关报警","开关报警消息","报警级别","存储方式","存储间隔(秒)","压缩精度","是否上传","PV上传标识","辅助参数","Reserve2"]
["上能逆变器","P","ep","模拟量","读写","0.01","0.0","0.0","0","512","1","0","4","1002","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","17","0","0"]
["上能逆变器","Q","eq","模拟量","读写","0.01","0.0","0.0","0","512","1","0","4","1003","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","18","0","0"]
["上能逆变器","PF","cos","模拟量","读写","0.001","0.0","0.0","0","512","1","0","4","1004","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","28","0","0"]
["上能逆变器","Ua","ua","模拟量","读写","0.057737","0.0","0.0","0","512","1","0","4","1005","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","9","0","0"]
["上能逆变器","Ub","ub","模拟量","读写","0.057737","0.0","0.0","0","512","1","0","4","1006","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","10","0","0"]
["上能逆变器","Uc","uc","模拟量","读写","0.057737","0.0","0.0","0","512","1","0","4","1007","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","11","0","0"]
["上能逆变器","F","f","模拟量","读写","0.001","0.0","0.0","0","512","1","0","4","1008","32位无符号","1234","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","32","0","0"]
["上能逆变器","Ia","ia","模拟量","读写","0.01","0.0","0.0","0","512","1","0","4","1010","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","0","0","0"]
["上能逆变器","Ib","ib","模拟量","读写","0.01","0.0","0.0","0","512","1","0","4","1011","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","1","0","0"]
["上能逆变器","Ic","ic","模拟量","读写","0.01","0.0","0.0","0","512","1","0","4","1012","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","1","0","0"]
["上能逆变器","Pdc","inputep","模拟量","读写","0.01","0.0","0.0","0","512","1","0","4","1045","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","164","0","0"]
["上能逆变器","Umppt1","uPV1","模拟量","读写","1.0","0.0","0.0","0","512","1","0","4","1046","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","1350","0","1"]
["上能逆变器","Umppt2","uPV2","模拟量","读写","1.0","0.0","0.0","0","512","1","0","4","1047","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","2351","0","2"]
["上能逆变器","Umppt3","uPV3","模拟量","读写","1.0","0.0","0.0","0","512","1","0","4","1048","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","3352","0","3"]
["上能逆变器","Umppt4","uPV4","模拟量","读写","1.0","0.0","0.0","0","512","1","0","4","1049","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","4353","0","4"]
["上能逆变器","Umppt5","uPV5","模拟量","读写","1.0","0.0","0.0","0","512","1","0","4","1050","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","5354","0","5"]
["上能逆变器","Umppt6","uPV6","模拟量","读写","1.0","0.0","0.0","0","512","1","0","4","1051","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","6355","0","6"]
["上能逆变器","Umppt7","uPV7","模拟量","读写","1.0","0.0","0.0","0","512","1","0","4","1052","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","7513","0","7"]
["上能逆变器","Umppt8","uPV8","模拟量","读写","1.0","0.0","0.0","0","512","1","0","4","1053","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","8514","0","8"]
["上能逆变器","Umppt9","uPV9","模拟量","读写","1.0","0.0","0.0","0","512","1","0","4","1054","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","9627","0","9"]
["上能逆变器","Umppt10","uPV10","模拟量","读写","1.0","0.0","0.0","0","512","1","0","4","1055","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","10628","0","10"]
["上能逆变器","Umppt11","uPV11","模拟量","读写","1.0","0.0","0.0","0","512","1","0","4","1056","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","11629","0","11"]
["上能逆变器","Umppt12","uPV12","模拟量","读写","1.0","0.0","0.0","0","512","1","0","4","1057","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","12630","0","12"]
["上能逆变器","Imppt1","iPV1","模拟量","读写","0.1","0.0","0.0","0","512","1","0","4","1078","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","1344","0","1"]
["上能逆变器","Imppt2","iPV2","模拟量","读写","0.1","0.0","0.0","0","512","1","0","4","1079","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","2345","0","2"]
["上能逆变器","Imppt3","iPV3","模拟量","读写","0.1","0.0","0.0","0","512","1","0","4","1080","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","3346","0","3"]
["上能逆变器","Imppt4","iPV4","模拟量","读写","0.1","0.0","0.0","0","512","1","0","4","1081","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","4347","0","4"]
["上能逆变器","Imppt5","iPV5","模拟量","读写","0.1","0.0","0.0","0","512","1","0","4","1082","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","5348","0","5"]
["上能逆变器","Imppt6","iPV6","模拟量","读写","0.1","0.0","0.0","0","512","1","0","4","1083","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","6349","0","6"]
["上能逆变器","Imppt7","iPV7","模拟量","读写","0.1","0.0","0.0","0","512","1","0","4","1084","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","7507","0","7"]
["上能逆变器","Imppt8","iPV8","模拟量","读写","0.1","0.0","0.0","0","512","1","0","4","1085","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","8508","0","8"]
["上能逆变器","Imppt9","iPV9","模拟量","读写","0.1","0.0","0.0","0","512","1","0","4","1086","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","9615","0","9"]
["上能逆变器","Imppt10","iPV10","模拟量","读写","0.1","0.0","0.0","0","512","1","0","4","1087","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","10616","0","10"]
["上能逆变器","Imppt11","iPV11","模拟量","读写","0.1","0.0","0.0","0","512","1","0","4","1088","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","11617","0","11"]
["上能逆变器","Imppt12","iPV12","模拟量","读写","0.1","0.0","0.0","0","512","1","0","4","1089","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","12618","0","12"]
["上能逆变器","Eff","xiaolv","模拟量","读写","0.001","0.0","0.0","0","512","1","0","4","1094","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","243","0","0"]
["上能逆变器","Temp","temperature","模拟量","读写","0.1","0.0","0.0","0","512","1","0","4","1095","16位有符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","36","0","0"]
["上能逆变器","DayE","daypositiveActice","模拟量","读写","0.1","0.0","0.0","0","512","1","0","4","1100","16位无符号","12","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","238","0","0"]
["上能逆变器","TotalE","positiveActice","模拟量","读写","1.0","0.0","0.0","0","512","1","0","4","1101","32位无符号","1234","0","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","240","0","0"]
["上能逆变器","电网欠压","warning1","开关量","读写","1.0","0.0","0.0","0","512","1","0","4","2010","16位无符号","12","1","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","100007","0","0"]
["上能逆变器","电网过压","warning2","开关量","读写","1.0","0.0","0.0","0","512","1","0","4","2010","16位无符号","12","1","1","1","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","100008","0","0"]
["上能逆变器","电网电压不平衡","warning3","开关量","读写","1.0","0.0","0.0","0","512","1","0","4","2010","16位无符号","12","1","2","2","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","0","300","1.0","1","100010","0","0"]
["上能逆变器","电网欠频","warning4","开关量","读写","1.0","0.0","0.0","0","512","1","0","4","2010","16位无符号","12","1","4","4","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","1","300","1.0","1","100012","0","0"]
["上能逆变器","电网过频","warning5","开关量","读写","1.0","0.0","0.0","0","512","1","0","4","2010","16位无符号","12","1","5","5","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","1","300","1.0","1","100011","0","0"]
["上能逆变器","频率异常","warning6","开关量","读写","1.0","0.0","0.0","0","512","1","0","4","2010","16位无符号","12","1","6","6","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","1","300","1.0","1","100013","0","0"]
["上能逆变器","孤岛","warning7","开关量","读写","1.0","0.0","0.0","0","512","1","0","4","2010","16位无符号","12","1","11","11","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","1","300","1.0","1","100006","0","0"]
["上能逆变器","残余电流超限","warning8","开关量","读写","1.0","0.0","0.0","0","512","1","0","4","2010","16位无符号","12","1","12","12","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","1","300","1.0","1","100016","0","0"]
["上能逆变器","绝缘阻抗异常","warning9","开关量","读写","1.0","0.0","0.0","0","512","1","0","4","2014","16位无符号","12","1","2","2","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","1","300","1.0","1","100018","0","0"]
["上能逆变器","并网运行","warning10","开关量","读写","1.0","0.0","0.0","0","512","1","0","4","1990","16位无符号","12","1","0","0","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","1","300","1.0","0","-1","0","-1"]
["上能逆变器","告警运行","warning11","开关量","读写","1.0","0.0","0.0","0","512","1","0","4","1990","16位无符号","12","1","1","1","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","1","300","1.0","0","-1","0","-1"]
["上能逆变器","隆额运行","warning12","开关量","读写","1.0","0.0","0.0","0","512","1","0","4","1990","16位无符号","12","1","2","2","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","1","300","1.0","1","100266","0","0"]
["上能逆变器","故障","warning13","开关量","读写","1.0","0.0","0.0","0","512","1","0","4","2050","16位无符号","12","1","4","4","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","1","300","1.0","1","100265","0","0"]
["上能逆变器","过温运行","warning14","开关量","读写","1.0","0.0","0.0","0","512","1","0","4","2050","16位无符号","12","1","11","11","0","1","0","0","0","0","100.0","90.0","10.0","0.0","高高报警","高报警","低报警","低低报警","0.0","3","不报警","通知","1","300","1.0","1","100019","0","0"]